## CCRO표지
CCRO System Flow Diagram
[7 empty] | PF Cycle |  |  | CC Cycle
| Feed Water |  |  | CCRO |  |  | Feed Ratio | 110 | % | Conc.Recycle | 4.54 | ㎥/h/pv | 10
[7 empty] | Recovery | 10 | % | Recovery | 68.4802 | %
| Q : | 10 | ㎥/h | Recovery | 85 | % | Feed Flow | 10.85 | ㎥/h | Feed Flow | 9.8636 | ㎥/h | 0.85 | 110 | 1
| TDS : | 579.276 | mg/L | Permeate | 8.5 | ㎥/h | Permeate Flow | 1.085 | ㎥/h | Blend Feed Flow | 14.4036 | ㎥/h/pv |  |  | 0.85
| E.C : | 984.7692 | ㎲/cm | Concentrate | 1.5 | ㎥/h | Concentrate Flow | 9.765 | ㎥/h | Permeate Flow | 9.8636 | ㎥/h |  |  | 10.85
|  |  |  | Flux | 76.2444 | LMH | Flux | 9.7324 | LMH | Concetrate Flow | 4.54 | ㎥/h/pv |  |  | 9.8636
[7 empty] | Cycle | 1 | 회 | Flux | 88.4761 | LMH
[7 empty] | Duration |  | min | Cycle |  | 회
[10 empty] | Duration |  | min
R/O membrane Element source |  |  |  | CCRO Stages |  |  |  | System Volume
Model |  | Suez AG8040F 400 FR |  | Vessel |  | 1 | EA | 0.13173 | ㎥
permeate Flow gpd |  | 11000 | gpd | Element / Vessel |  | 3 | EA | 0.02 | ㎥/Ele
|  | 41.635 | ㎥/day | Total Element |  | 3 | EA
membrane area |  | 400 |  | spacer |  | 1 | EA | 0.032931 | ㎥/space
|  | 37.1612 | ㎡ | Vessel Size |  | 4 | Els
pressure | operating | 225 | psi | System Volume |  | 0.065863 | ㎥
| max | 600 | psi | Activ Area |  | 111.4836 | ㎥
Diameter |  | 8 | inch
|  | 20.32 | cm
Length |  | 101.6 | cm
Recovery |  | 15 | %
〖𝑓𝑡〗^2
Note on K5: Range 110% ~ 150%
Note on O5: Range 4.54 ~ 7.95
Note on K6: Range 10 ~ 30%
Note on G7: Range 75 ~ 98%

## 유입원수성상
R/O전단 유입원수 성상
Cation(양이온)
항목 | mg/L | at CaCO3 | meq/L
NH4 | 3 | 8.322 | 0.165
K | 3 | 3.84 | 0.078
Na | 3 | 6.531 | 0.129
Mg | 1 | 4.118 | 0.082
Ca | 1 | 2.497 | 0.05 | Neutrals |  |  | CO2값 HCO2 자동계산 값이 높을수록 오차 증가
Sr | 1 | 1.142 | 0.023 | 항목 | mg/L
Ba | 1 | 0.729 | 0.015 | SiO2
B
ToTal | 13 | 27.179 | 0.542 | CO2 | 59.976
Anion(양이온) |  |  |  | ToTal | 59.976
항목 | mg/L | at CaCO3 | meq/L
CO2 | 0.3 | 0.5004 | 0.0099
HCO2 | 500 | 410 | 8
NO2 | 1 | 0.807 | 0.016 |  |  | TDS | 579.276 | mg/L
Cl | 1 | 1.412 | 0.028 |  |  | EC | 984.7692 | ㎲/㎠
F | 1 | 2.634 | 0.053
SO4 | 1 | 1.042 | 0.021
PO4 | 1 | 1.581 | 0.032
Br | 1 | 0.626 | 0.013
Total | 506.3 | 418.6024 | 8.1729

## PF,CC
(-)
Suez AG8040F 400 FR
| stage | element | element name | Recovery | Feed Flow | Feed press | feed TDS | Conc Flow | Perm Flow | Perm Flux | Perm TDS
|  |  |  | ( % ) | ( ㎥/h ) | ( Bar ) | ( mg/L ) | ( ㎥/h ) | ( ㎥/h ) | ( LMH ) | ( mg/L ) | 10
PF | PF | 1 | Suez AG8040F 400 FR |  | 10.85 |  | 579.276 | 9.765 |  |  |  | 579.276
(-) | PF | 2 | Suez AG8040F 400 FR
| PF | 3 | Suez AG8040F 400 FR
| (-) | (-) | (-)
| (-) | (-) | (-)
| (-) | (-) | (-)
CC1 | CC1 | 1 | Suez AG8040F 400 FR | [8 empty] | 68.4802
| CC1 | 2 | Suez AG8040F 400 FR
| CC1 | 3 | Suez AG8040F 400 FR
| (-) | (-) | (-)
| (-) | (-) | (-)
| (-) | (-) | (-)
CC2 | CC2 | 1 | Suez AG8040F 400 FR
| CC2 | 2 | Suez AG8040F 400 FR
| CC2 | 3 | Suez AG8040F 400 FR
| (-) | (-) | (-)
| (-) | (-) | (-)
| (-) | (-) | (-)
CC3 | CC3 | 1 | Suez AG8040F 400 FR
| CC3 | 2 | Suez AG8040F 400 FR
| CC3 | 3 | Suez AG8040F 400 FR
| (-) | (-) | (-)
| (-) | (-) | (-)
| (-) | (-) | (-)
CC4 | CC4 | 1 | Suez AG8040F 400 FR
| CC4 | 2 | Suez AG8040F 400 FR
| CC4 | 3 | Suez AG8040F 400 FR
| (-) | (-) | (-)
| (-) | (-) | (-)
| (-) | (-) | (-)

## Guide Line
CCRO
RO Membrane Design Guide Line
| Feed water Type | SDI Value | Average Permeate Flux (range) |  | Lead Element Permeate Flux |  | Concentrate Flow Rate per Vessel |  |  | Feed Flow Rate per Vessel |  |  | Pressure Drop per Vessel |  | Element Recovery Rate | Beta | Flux Decline Ratio | Salt passge increase
|  | - | LMH | Gpd | LMH | GPD | inch | ㎥/hr | gpm | inch | ㎥/hr | gpm | bar | Psi | % | - | % | %/a
| municipal Supply | <5 | 23 (20~26) | 13.5 (12~15) | <31 | <18 | 8 | >3.6 | >16 | 8 | <15 | <66 | <2.0 | <29 | <15 | <1.2 | 13 | >10
[7 empty] | 4 | >0.7 | >3.1 | 4 | <2.8 | <12
낮은 | Brackish Wells | <3 | 27 (23~29) | 15.9 (14~17) | <34 | <20 | 8 | >3.0 | >13 | 8 | <16 | <70 | <3.0 | <43 | <20 | <1.2 | 10 | >10
염분 | [6 empty] | 4 | >0.6 | >2.6 | 4 | <3.2 | <14
| Surface Water media fillteration | <5 | 23 (20~26) | 13.5 (12~15) | <31 | <18 | 8 | >3.6 | >16 | 8 | <15 | <66 | <2.0 | <29 | <15 | <1.2 | 13 | >10
[7 empty] | 4 | >0.7 | >3.1 | 4 | <2.6 | <12
| Surface Water MF/UF Filteration | <3 | 27 (23~29) | 15.0 (14~17) | <34 | <20 | 8 | >3.0 | >13 | 8 | <16 | <70 | <3.0 | <43 | <20 | <1.2 | 10 | >10
[7 empty] | 4 | >0.6 | >2.6 | 4 | <3.2 | <14
| Secondary Waste media Filteration | <5 | 17 (14~20) | 10 (8.2~12) | <24 | <14 | 8 | >4.1 | >18 | 8 | <14 | <61 | <2.0 | <29 | <12 | <1.2 | 18 | >15
[7 empty] | 4 | >0.8 | >3.5 | 4 | <2.6 | <11
| Secondary Waste MF/UF Filteration | <3 | 20 (17~23) | 11.8 (10~14) | <28 | <16 | 8 | >3.6 | >16 | 8 | <14 | <61 | <2.0 | <29 | <17 | <1.2 | 15 | >10
[7 empty] | 4 | >0.7 | >3.1 | 4 | <2.8 | <12
| Seawater Intake media Filteration | <5 | 14 (11~17) | 8.2 (6.5~10) | <30 | <18 | 8 | >3.6 | >16 | 8 | <14 | <61 | <2.0 | <29 | <13 | <1.2 | 8 | >10
[7 empty] | 4 | >0.7 | >3.1 | 4 | <2.8 | <12
| SeaWater Intake MF/UF filtertation | <3 | 17 (14~20) | 10 (8.2~12) | <35 | <21 | 8 | >3.4 | >15 | 8 | <16 | <70 | <3.0 | <43 | <15 | <1.2 | 6 | >10
[7 empty] | 4 | >0.7 | >3.1 | 4 | <3.0 | <13
| Seawater Beach Wells | <3 | 17 (14~20) | 10 (8.2~12) | <35 | <21 | 8 | >3.4 | >15 | 8 | <16 | <70 | <3.0 | <43 | <15 | <1.2 | 6 | >10
[7 empty] | 4 | ).07 | >3.1 | 4 | <3.0 | <13
| RO Pemeate | <1 | 37 (32~42) | 21.8 (19~24) | <48 | <26 | 8 | >2.4 | >11 | 8 | <17 | <74 | <3.0 | <43 | <30 | <1.3 | 6 | >5
[7 empty] | 4 | >0.5 | >2.2 | 4 | <3.6 | <16

## RO 막 비교표
Element | active area(m3) | permeate flow rate (gpd) | minimum Salt Rejection(%) | Stabilized Salt Rejection(%) | 비고 | test condition
Filmtec SOAR 4000i Element | 37 | 15000 | 99.2 | 99.4 | Low Energy(저압용) | 13.8bar, 25℃, pH8, 20% recovery
Filmtec SOAR 5000i Element | 37 | 12000 | 99.4 | 99.7 |  | 16.5bar, 25℃, pH8, 20% recovery
Filmtec SOAR 6000i Element | 41 | 24000 | 99.55 | 99.7 |  | 27.58bar, 25℃, pH8, 25% recovery
Filmtec SOAR 7000i Element | 41 | 12500 | 99.6 | 99.8 |  | 27.58bar, 25℃, pH8, 25% recovery
AG8040F 400 FR,34 | 37.2 | 11000 | 99 | 99.5 | 현재 사용막 | 15.5bar, 20℃, pH7.5, 15% recovery
Fiilmtec BW30FR-400/34 Element | 37 | 11000 | 99.35 | 99.5 | wave 막 중 현재 사용막과 가장 유사한 막 | 15.5bar, 25℃, pH8, 15% recovery
AG-440 | 40.9 | 12000 | 99.3 | 99.8 |  | 15.5bar, 25℃, pH7, 15% recovery
LEWABRANE RO B400 FR ASD | 37.2 | 11000 | 99.3 | 99.7 |  | 15.5bar, 25℃, pH7, 15% recovery
LG BW 440 R G2 | 41 | 12650 | 99.65 | 99.8 |  | 15.5bar, 25℃, pH7, 15% recovery

## 용량 계산
[11 empty] | CC | PF
element | permeat |  | recovery |  | 효율 | Qin | permeat | Concent | el 필요수 | Q in | permeat | concent | CFSTR
ASD | 41.5 | ㎥/day | 15 | % | 85 | 2.035 | 1.73 | 0.305 | 11.673 | 23.7546 | 20.1943 | 3.5603
| 1.7292 | ㎥/hr |  |  | 90 | 1.922 | 1.73 | 0.192 | 14.17 | 27.2347 | 24.5141 | 2.7206
[5 empty] | 95 | 1.82 | 1.73 | 0.09 | 18.43 | 33.5426 | 31.8839 | 1.6587
Batch